## Unloading Protocol
Annex 4:
LPG Unloading Protocol RO
Unloadid date and time:
FS name:
Supplier:
Tank registration number:
Responsible's name FS/ADR:
Driver's name:
*The table is completed and signed before the start of the unload, depending on the available space in the SKID (according to the station measurement system - it will not exceed 80%)
Product's name |  | GPL
The information below is confirmed by signature at the drop off location
Driver |  |  |  | yes | no
1.Personal protective equipment worn properly: helmet, protective glasses, coveralls, protective boots, protective gloves (Station/ADR representative according to Annex 15; driver according to Annex 17; Annexes from work instructions) ?
2.There are NO unauthorized accompanying persons in the tank cabin.
Tanker and driver documents
3.Do the tanker and the driver correspond to the approved list of drivers/tankers, according to Annex 2?
4.The driver has the required trainings to perform truck unloading and emergency response/recovery?
5.Is the tanker driver the one mentioned in the delivery document or the driver change report?
6.Is the driver's ADR certificate valid and the tanker has ADR agreement and inspection certificate valid?
Tank equipment checks
7.Does the driver park and turn off the engine to check the tanker?
8.Do the placarding and signaling of the vehicle correspond to ADR norms?
9.The tank has been checked and there are no gas leaks (with functional and calibrate gas detector or using water and soap), deformations, bumps in the compartment, broken electrical wires, specific smell of cables, plastic materials, rubber or hot brakes and is everything in order?
10.The unloading hoses have been visual checked and test pressure protocols are available?
11.Does the tank have seals in good condition according to the seal map in Annex 6?
12.Is there an earthing system installed on the tank (safe, verified)?
13.Does it have at least 2 wheel chocks, for the tanker?
14.Is the tank positioned at a distance of 5 MP (square meters) from the SKID?
Preparation for unloading - SKID area
15.Is the CCTV functional and can the registration number of the tanker be viewed?
16.The unloading area is lighted for unloading at night?
17.Have fire extinguishers been brought to the discharge area and placed properly (wind direction)?. Are they within the validity period and the pressure gauge needle is in the green area? . Is the unwinding of the hose from the fire extinguishers and their location done in such a way as to allow immediate use in case of emergency situations?
18.Is the unloading place properly signposted (cones), the tank is located at the safety distance according to the EX zoning of the station and oriented towards the exit? All potential ignition sources are removed (including parked cars) near the unloading position and skid?
19.Is the parking brake applied and have the wheel chocks been installed?
20.Is the earthing cable from the tank to the SKID earthing point properly connected?
21.Has the existence of space in the SKID been verified so that the maximum load of 80% of the tank is not exceeded?
22.Has the station manager/ADR checked the SKID installation as appropriate? (functional, without defects, seals, deformations of the SKID, fixing on the foundation, etc.). Interruption of the electricity supply made at the skid?
23.Did the driver set the tank flow meter corresponding to the delivered product?
24.Has the driver checked the SKID supply hose coupling part?
25.Did the driver checked and correctly connect the tank hose to the SKID and the proper operation of the tank pump?
26.Did the driver instruct the ADR representative of the station regarding the interruption of unloading in case of emergency by pressing the side emergency buttons and the tank engine stop button?.
27.Has the driver and the station manager/ADR verified compliance with the requirements regarding the prohibition of open fire, smoking and work with open fire in the unloading area?
28.Does the driver start tanker engine and gradually open the discharge valve and check the coupling, tank hose and tank connection?
29.Does the driver check the flow rate and the meter indication and the increase in the LPG car level in the SKID?
Unloading process validation
Driver signature
Signature of responsible Station/ADR
Unloading complete
30.Upon completion of the LPG discharge, the driver performed the following operations: he stopped and disconnected the pump, disconnected the hose (after all the vapors had come out), closed the taps between the hose container and the tank, sealed the tank, checked the car LPG level in SKID, disconnected the ground from the SKID, ran the cable in the tank, removed the wheel tracks?
31.Has the SKID/valve been checked for leaks?
32.Did the driver issue the documents corresponding to the delivery and hand them to the station manager/ADR?
Driver signature
Signature of responsible Station/ADR
CAREFUL!
1. | Responsible for completing the document is the station/ADR representative!
2. | Tank LPG unloading outside the established intervals: summer = 05-20.00, and winter = 07-18.00 will be carried out only with approval, according to the procedure.
3. | If any of the NO columns, which cannot be solved in the station, has been checked, the unloading process is stopped and the Area Manager, the ADR Advisor, the head of the PMSL-S and SR department are notified by phone/e-mail. STOP WORK! Approval of the download by phone/e-mail after solving the non-conformities from the Area Manager or Zonal ADR Advisor or responsible Dep. PMSL-S!

## Protocol de descarcare
Anexa 4:
Protocol de descărcare GPL auto in stațiile de distribuție
Data și ora descărcării:
Nume stație:
Transportator:
Nr. Înmatr. cisterna:
Nume resp. Stație/ADR:
Nume șofer:
*Tabelul se completeaza si semnează înaintea începerii descărcării, în funcție de spațiul disponibil din SKID (conform sistem de măsurare stație - nu va depăsi 80%)
Denumire produs |  | GPL
Informațiile de mai jos se confirmă prin semnatura la locul de descărcare
Șofer |  |  |  | DA | NU
1.Echipament individual de protecție purtat corespunzător: cască, ochelari de protecție, salopetă, bocanci de protecție, mănuși de protecție (repr. Statie/ADR conform Anexa 15; șofer conform Anexa 17) ?
2.În cabina cisternei NU există persoane însoțitoare neautorizate.
Documente cisternă și șofer
3.Cisterna și șoferul corespund cu lista de șoferi/cisterne agreată, conform Anexa 2?
4.Șoferul este instruit corespunzator pentru descărcarea cisternei și pentru a actiona în caz de urgență?
5.Șoferul cisternei este cel menționat în documentul de livrare sau procesul verbal de schimbare între șoferi?
6.Atestatul ADR al soferului este in termen de valabilitate? Cisterna are certificat ADR de inspectie valabil?
Cisternă verificări echipamente
7.Soferul parcheaza si opreste motorul pentru verificarea cisternei?
8.Placardarea si semnalizarea autovehicolului corespund conform normelor ADR ?
9.Cisterna a fost verificată (cu detectorul de gaz functional si calibrat sau folosind apa si sapun) și nu există scurgeri de gaz, deformări, lovituri ale compartimentului , fire electrice intrerupte, miros specific de cabluri, materiale plastice, cauciuc sau frane incinse si este totul in regula?
10.Furtunurile de descarcare au fost verificate vizual si s-a prezentat protocolul testului la presiune?
11.Cisterna are sigiliile în buna stare conform hărții sigiliilor din Anexa 6?
12.Are instalație de împământare instalata pe cisternă (bună stare,verificată)?
13.Are cel puțin 2 cale de siguranță roți, pentru autocisternă ?
14.Cisterna este poziționată la o distanță minima de siguranta de 5 MP (metri patrați) față de SKID?
Pregătirea în vederea descărcării- zona SKID
15.CCTV-ul este functional si se poate vizualiza numarul de inmatriculare al cisternei?
16.Zona de descărcare este luminată pentru descărcarea pe timp de noapte
17. Stingătoarele au fost aduse în zona de descărcare și puse corespunzător (direcția vântului)?. Sunt in termen de valabilitate si acul manometrului se afla pe zona de culoare verde? . Desfasurararea furtunului de pe stingatoare si amplasarea lor este facuta in asa fel incat sa permita folosirea imediata in cazul unor situatii de urgenta ?.
18.Locul de descărcare este semnalizat corespunzator (conuri), cisterna este amplasată la distanța de siguranță conform zonare EX a stației și orientată către ieșire si toate sursele potentiale de aprindere (inclusiv masini parcate) au fost indepartate din zona de descarcare si de langa SKID?
19.Frană de staționare este trasă și s-au montat calele la roți ?
20.Cablul de împământare ,de la cisternă la punctul de împământare SKID, este conectat corespunzător?
21.S-a verificat existenta spațiului în SKID astfel încât sa nu se depașească încarcarea maximă de 80% a rezervorului ?
22.Responsabilul stației/ADR a verificat instalația SKID ca fiind corespunzătoare? (funcțională, fără defecte, sigilii, deformări ale SKID-ului, fixare pe fundație, etc.). Întreruperea alimentarii cu energie electrica realizata la skid?
23.Șoferul a efectuat setarea debitmetrului cisternei corespunzător produsului livrat?
24.Șoferul a verificat partea de cuplare a furtunului de alimentare a SKID-ului?
25.Șoferul a verificat si conectat corect furtunul cisternei la SKID și functionarea corespunzatoare a pompei cisternei?
26.Soferul l-a instruit pe reprezentantul ADR al statiei cu privire la intreruperea descarcarii in caz de urgenta prin actionarea butoanelor laterale de urgenta si butonul de oprire a motorului cisternei ?
27.S-a verificat de către șofer și responsabilul stației/ADR respectarea cerințelor privind interzicerea focului deschis, a fumatului și a lucrărilor cu focul deschis în zona de descărcare ?
28.Șoferul porneste motorul si face deschidere graduală a vanei de descărcare și verificarea conexiunii cuplă, furtun cisternă și rezervor ?
29.Șoferul verifică debitul și indicația contorului și creșterea nivelului de GPL auto din SKID?
Validare proces de descarcare
Semnătură șofer
Semnatura responsabil Stație/ADR
Finalizare descărcare
30.La finalizarea descărcarii GPL șoferul a efectuat următoarele operațiuni: a oprit și deconectat pompa, a decuplat furtunul (dupa ce au ieșit toți vaporii),a închis robineții între recipient furtun și cisternă, a sigilat rezervorul, a făcut verificarea nivelului GPL auto din SKID, a deconectat împământarea de la SKID, a rulat cablul în cisterna, a îndepartat calele de la roți?
31.S-a verificat etanseitatea SKIDului/supapei ?
32.A emis șoferul actele corespunzătoare livrării și le-a înmânat responsabilului stației/ADR?
Semnătură șofer
Semnatura responsabil Stație/ADR
ATENȚIE!
1. | Responsabil de completarea documentului este resonsabilul stației/ADR!
2. | Descărcarea GPL auto în afara intervalelor stabilite:vara = 05-20.00, iar iarna = 07-18.00 va fi efectuata doar cu aprobare, conform procedurii.
3. | În cazul în care a fost bifată oricare dintre rubricile NU, ce nu pot fi rezolvate in statie , se oprește procesul de descărcare și se anunță pe telefon/e-mail Area Managerul, Consilierul ADR, responsabilul departament PMSL-S și SS-HD.STOP WORK ! Aprobarea descărcarii pe telefon/ e-mail după rezolvarea neconformităților de la Area Manager sau Consilier ADR zonal sau responsabil Dep.PMSL-S!